## Sheet1
Project: | P234 - Maintenance Hangar |  |  |  | USER NOTES (Not intended to print)
Location: | Anytown, VA
Project #: | 12345678
Date: | 2020-03-01
STATEMENT OF SPECIAL INSPECTIONS |  |  |  |  | < Edit Blue text/cells only
Seismic Design Category: |  | E |  |  | SPECIAL INSPECTOR OF RECORD (SIOR) DETERMINATION |  | A | I | Yes
Risk Category: |  | III |  |  |  |  | B | II | No
Number of Stories above Grade: |  | 1 |  |  | < The Special Inspector of Record (SIOR) is a DOD mandate. Enter the requested data to determine whether an SIOR is required or is not required. |  | C | III
Height of Highest Occupied Roof or Floor above the Lowest Level of Fire Department Vehicle Access: |  | 75 |  |  |  |  | D | IV
Hazardous Occupancy or attached to such? |  | No | Group H Occupancies |  |  |  | E | V
F
Special Inspector of Record (SIOR)
A Special Inspector of Record (SIOR) |  | IS |  | required (per UFGS 01 45 35, Section 1.3.7)
SIOR Name (Registered Professional): |  | John Doe P.E.
Professional Registration Number: |  | C222222 |  |  | < For DB contracts insert the SIOR contact information. For DBB contracts enter, "Contractor to provide prior to construction start".
Consulting Firm Name (if any): |  | ABC Structural Consulting
SIOR Office AND Mobile Phone Number: |  | 1234567895 (Mobile), 123456789 (Office) |  |  | < The SIOR must be a registered professional engineer, and must not be an employee of the General Contractor or sub-contractor, but may be the project structural engineer of record if desired. Where did this come from?
Lateral Force Resisting System (LFRS)
2024 IBC 1704.3.2 and 1704.3.3 |  |  |  |  | LATERAL FORCE RESISTING SYSTEM IDENTIFICATION
Following is a listing of critical elements of the main wind/seismic force-resisting system for this structure. Carefully inspect these elements as part of the roles and responsiblities of the Special Inspector (reference the Schedule of Special Inspections for inspection checklists).
Vertical LFRS Elements |  |  |  | Notes
Steel Ordinary Concentrically Braced Frames |  |  |  | North - South Direction Only, See Plan
Steel Special Concentrically Braced Frames |  |  |  | Lettered Gridline only, see plan for call out
Steel Ordinary Moment Frames (SMF) |  |  |  | Both orthoginal Directions, See plan for call out
Ordinary Reinforced Concrete Shear Walls |  |  |  | See Key Notes
Concrete Grade Beams Resisting Lateral Loads |  |  |  | Office Portion Only, see plan key notes
Ordinary Reinforced Masonry Shear Walls |  |  |  | High Bay, Numbered Gridlines only, see plan
OSB Sheathed Shear Walls (nailing, sill bolting, Etc) |  |  |  | See schedule on plan
Wood Shear Wall Hold Downs |  |  |  | Identified on Plan & in Detail Sheet X.XX
Horizontal LFRS Elements |  |  |  | Notes
Continuous Roof Ties |  |  |  | See Key Notes on Roof Plan
Collector Elements |  |  |  | Identified on plan with key notes
Concrete topping over metal deck |  |  |  | 2nd floor and roof
Metal Roof Deck & Related Fastening System |  |  |  | See Roof Plan
Out-of-Plane Wall Connections |  |  |  | See Structural Details XX & XX
Diaphragm Cross Rod Bracings |  |  |  | See Roof Plan for locations
Cast-in-Place Concrete Floor and Roof Diaphragms |  |  |  | See sheet XX for details and rebar schedule
Special Force Transfer Connections |  |  |  | See Detail X on Sheet X.XX
Statement of Special Inspections Page 1 of 2
Project: | P234 - Maintenance Hangar
Location: | Anytown, VA |  |  |  | DESIGNATED SEISMIC SYSTEMS (DSS)
Project #: | 12345678 |  |  |  | This section identifies whether Designated Seismic Systems apply to this project or do not apply. Additionally, and where DSS apply, some explanation is provided below for what a Designated Seismic System is for this specific project.
Date: | 2020-03-01
Designated Seismic Systems (DSS)
(2024 IBC 1705.13.4) (ASCE 7-22, 13.2.3, C13.2.2) (UFC 3-301-1, 2-5.3)
'Designated Seismic Systems' (DSS) must remain operable and continue to contain hazardous substances following a design earthquake. Accordingly, all Designated Seismic Systems must be listed below and must be certified by the manufacturer to remain both operable and/or to contain hazardous substances after a design earthquake per UFC 3-301-01, Section 3-5.2. Submit said Certificates of Compliance to the Contracting Officer for each DSS after they have been reviewed and accepted by the EOR/DOR. Additionally, the below listed Designated Seismic Systems must be carefully inspected by the Special Inspector according to the requirements noted in the Schedule of Special Inspections, Section BB.
ELECTRICAL Components that are part of the Designated Seismic System (DSS) , which require a Certificate of Compliance |  |  |  |  | < Designated Seismic Systems APPLY to this project. List all Designated Seismic Systems in the blue tables below. Some DSS suggestions are already populated, delete or keep as necessary.
DSS for this project are nonstructural components with an importance factor of 1.5 AND with the following project conditions (UFC 3-301-01 SECTION 3-3.3) (ASCE 7-22, 13.2.3):
1. | DSS Emergency or Standby Power System
2. | DSS Component XX
3. | DSS Component XX
4. | DSS Component XX |  |  |  |  | 1. The component is required to function for life-safety purposes after an earthquake, including fire sprinkler systems and egress stairways (RC I thru V + SDC C thru F).
5. | DSS Component XX
If additional space is required, append an additional sheet listing the remaining DSS
MECHANICAL/PLUMBING Components that are part of the Designated Seismic System (DSS), which require a Certificate of Compliance | [5 empty] | 2. The component conveys, supports, or otherwise contains toxic, highly toxic, or explosive substances where the quantity of the material exceeds a threshold quantity established by the Authority Having Jurisdiction and is sufficient to pose a threat to the public if released (RC I thru V + SDC C thru F).
1. | DSS Gas lines and associated fittings, anchorage, & flexible Connections
2. | DSS Component XX
3. | DSS Component XX
4. | DSS Component XX
5. | DSS Component XX |  |  |  |  | 3. The component conveys, supports, or otherwise contains hazardous substances and is attached to a structure, or portion thereof, classified by the authority having jurisdiction as a hazardous occupancy (RC I thru V + SDC C thru F).
6. | DSS Component XX
If additional space is required, append an additional sheet listing the remaining DSS
OTHER Designated Seismic Systems (DSS) requiring a Certificate of Compliance
1. | DSS Building egress stair systems
2. | DSS Building fire sprinkler systems
3. | DSS Component XX
4. | DSS Component XX
5. | DSS Component XX
6. | DSS Component XX
Final Walk-Down Inspection and Report
(UFC 3 301 01 SECTION 2-5.4) |  |  |  |  | FINAL WALK DOWN INSPECTION AND REPORT FOR DSS
Designated Seismic Systems shall receive a final walk-down inspection by the Registered Design Professional in Responsible Charge
< A DSS final walk down inspection applies to this project
Final Walk-Down Report, Prepared by the Registered Design Professional in Responsible Charge, must Include:
1. Record observations of Final Walk-Down Inspection
2. Document that Inspections were performed in accordance with the Schedule of Special Inspections
3. Document that all Designated Seismic Systems are installed according to construction/manufacturer document requirements, and that Compliance Certificates have been collected (UFC 03 301 01, 3-5.2, 13.2.3.2). |  |  |  |  | < …Certificates of compliance documenting that the requirements are met shall be maintained in a file identified as "Equipment Certification Documentation". This file shall be part of the final project O&M Manual
Statement of Special Inspections Page 2 of 2
NEXT: COMPLETE THE SCHEDULE OF SPECIAL INSPECTIONS TEMPLATE.
Edit, print, and append the Schedule of Special Inspections Template to this Statement of Special Inspections and insert both at the back of the Special Inspections Specification. SI schedule template: https://www.wbdg.org/ffc/dod/unified-facilities-criteria-ufc/ufc-3-301-01
Example entries are provided, replace/delete as necessary